## 400V-50Hz
Code number AHF005 IP00/IP20 | Code number AHF010 IP00/IP20 | Filter current rating | Typical motor | VLT Power and Current Ratings |  | Losses |  | Acoustic noise | Frame size
|  | 50Hz |  |  |  | AHF005 | AHF010
|  | A | kW | kW | A | W | W | dBa | AHF005 | AHF010
130B1392 130B1229 | 130B1262 130B1027 | 10 | 3 | PK37-P4K0 | 1,2-9 | 131 | 93 | <70 | X1 | X1
130B1393 130B1231 | 130B1263 130B1058 | 14 | 7.5 | P5K5-P7K5 | 14.4 | 184 | 118 | <70 | X1 | X1
130B1394 130B1232 | 130B1268 130B1059 | 22 | 11 | P11K | 22 | 258 | 206 | <70 | X2 | X2
130B1395 130B1233 | 130B1270 130B1089 | 29 | 15 | P15K | 29 | 298 | 224 | <70 | X2 | X2
130B1396 130B1238 | 130B1273 130B1094 | 34 | 18.5 | P18K | 34 | 335 | 233 | < 72 | X3 | X3
130B1397 130B1239 | 130B1274 130B1111 | 40 | 22 | P22K | 40 | 396 | 242 | < 72 | X3 | X3
130B1398 130B1240 | 130B1275 130B1176 | 55 | 30 | P30K | 55 | 482 | 274 | < 72 | X3 | X3
130B1399 130B1241 | 130B1281 130B1180 | 66 | 37 | P37K | 66 | 574 | 352 | < 72 | X4 | X4
130B1442 130B1247 | 130B1291 130B1201 | 82 | 45 | P45K | 82 | 688 | 374 | < 72 | X4 | X4
130B1443 130B1248 | 130B1292 130B1204 | 96 | 55 | P55K | 96 | 747 | 428 | < 75 | X5 | X5
130B1444 130B1249 | 130B1293 130B1207 | 133 | 75 | P75K | 133 | 841 | 488 | < 75 | X5 | X5
130B1445 130B1250 | 130B1294 130B1213 | 171 | 90 | P90K | 171 | 962 | 692 | < 75 | X6 | X6
130B1446 130B1251 | 130B1295 130B1214 | 204 | 110 | P110 | 204 | 1080 | 743 | < 75 | X6 | X6
130B1447 130B1258 | 130B1369 130B1215 | 251 | 132 | P132 | 251 | 1194 | 864 | < 75 | X7 | X7
130B1448 130B1259 | 130B1370 130B1216 | 304 | 160 | P160 | 304 | 1288 | 905 | < 75 | X7 | X7
130B1449 130B1260 | 130B1389 130B1217 | 381 | 200 | P200 | 381 | 1510 | 1175 | < 77 | X8 | X7
130B1469 130B1261 | 130B1391 130B1228 | 480 | 250 | P250 | 472 | 1852 | 1542 | < 77 | X8 | X8
2 x 130B1448 2 x 130B1259 | 2 x 130B1370 2 x 130B1216 | 608 | 315 | P315 | 590 | 2576 | 1810 | < 80
2 x 130B3153 2 x 130B3152 | 2 x 130B3151 2 x 130B3136 | 650 | 355 | P355 | 647 | 2812 | 1904 | < 80
130B1448 + 130B1449 130B1259 + 130B1260 | 130B1370 + 130B1389 130B1216 + 130B1217 | 685 | 400 | P400 | 684 | 2798 | 2080 | < 80
2 x 130B1449 2 x 130B1260 | 2 x 130B1389 2 x 130B1217 | 762 | 450 | P450 | 779 | 3020 | 2350 | < 80
130B1449 + 130B1469 130B1260 + 130B1261 | 130B1389 + 130B1391 130B1217 + 130B1228 | 861 | 500 | P500 | 857 | 3362 | 2717 | < 80
2 x 130B1469 2 x 130B1261 | 2 x 130B1391 2 x 130B1228 | 960 | 560 | P560 | 964 | 3704 | 3084 | < 80
3 x 130B1449 3 x 130B1260 | 3 x 130B1389 3 x 130B1217 | 1140 | 630 | P630 | 1090 | 4530 | 3525 | < 80
2 x 130B1449 + 130B1469 2 x 130B1260 + 130B1261 | 2 x 130B1389 + 130B1391 2 x 130B1217 + 130B1228 | 1240 | 710 | P710 | 1227 | 4872 | 3892 | < 80
3 x 130B1469 3 x 130B1261 | 3 x 130B1391 3 x 130B1228 | 1440 | 800 | P800 | 1422 | 5556 | 4626 | < 80
2 x 130B1449 + 2 x 130B1469 2 x 130B1260 + 2 x 130B1261 | 2 x 130B1389 + 2 x 130B1391 2 x 130B1217 + 2 x 130B1228 | 1720 | 1000 | P1000 | 1675 | 6724 | 5434 | < 80

## 380V-60Hz
Code number AHF005 IP00/IP20 | Code number AHF010 IP00/IP20 | Filter current rating | Typical motor | VLT Power and Current Ratings |  | Losses |  | Acoustic noise | Frame size
|  | 50Hz |  |  |  | AHF005 | AHF010
|  | A | kW | kW | A | W | W | dBa | AHF005 | AHF010
130B3095 130B1257 | 130B2874 130B2262 | 10 | 3 | PK37-P4K0 | 1,2-9 | 131 | 93 | <70 | X1 | X1
130B3096 130B2858 | 130B2875 130B2265 | 14 | 7.5 | P5K5-P7K5 | 14.4 | 184 | 118 | <70 | X1 | X1
130B3097 130B2859 | 130B2876 130B2268 | 22 | 11 | P11K | 22 | 258 | 206 | <70 | X2 | X2
130B3098 130B2860 | 130B2877 130B2294 | 29 | 15 | P15K | 29 | 298 | 224 | <70 | X2 | X2
130B3099 130B2861 | 130B3000 130B2297 | 34 | 18.5 | P18K | 34 | 335 | 233 | < 72 | X3 | X3
130B3124 130B2862 | 130B3083 130B2303 | 40 | 22 | P22K | 40 | 396 | 242 | < 72 | X3 | X3
130B3125 130B2863 | 130B3084 130B2445 | 55 | 30 | P30K | 55 | 482 | 274 | < 72 | X3 | X3
130B3026 130B2864 | 130B3085 130B2459 | 66 | 37 | P37K | 66 | 574 | 352 | < 72 | X4 | X4
130B3127 130B2865 | 130B3086 130B2488 | 82 | 45 | P45K | 82 | 688 | 374 | < 72 | X4 | X4
130B3128 130B2866 | 130B3087 130B2489 | 96 | 55 | P55K | 96 | 747 | 428 | < 75 | X5 | X5
130B3129 130B2867 | 130B3088 130B2498 | 133 | 75 | P75K | 133 | 841 | 488 | < 75 | X5 | X5
130B3130 130B2868 | 130B3089 130B2499 | 171 | 90 | P90K | 171 | 962 | 692 | < 75 | X6 | X6
130B3131 130B2869 | 130B3090 130B2500 | 204 | 110 | P110 | 204 | 1080 | 743 | < 75 | X6 | X6
130B3132 130B2870 | 130B3091 130B2700 | 251 | 132 | P132 | 251 | 1194 | 864 | < 75 | X7 | X7
130B3133 130B2871 | 130B3092 130B2819 | 304 | 160 | P160 | 304 | 1288 | 905 | < 75 | X7 | X7
130B3134 130B2872 | 130B3093 130B2855 | 381 | 200 | P200 | 381 | 1510 | 1175 | < 77 | X8 | X7
130B3135 130B2873 | 130B3094 130B2856 | 480 | 250 | P250 | 472 | 1852 | 1542 | < 77 | X8 | X7
2 x 130B3133 2 x 130B2871 | 2 x 130B3092 2 x 130B2819 | 608 | 315 | P315 | 590 | 2576 | 1810 | < 80
130B3157 130B3156 | 130B3155 130B3154 | 650 | 315 | P355 | 647 | 2812 | 1904 | < 80
130B3133 + 130B3134 130B2871 + 130B2872 | 130B3092 + 130B3093 130B2819 + 130B2855 | 685 | 355 | P400 | 684 | 2798 | 2080 | < 80
2 x 130B3134 2 x 130B2872 | 2 x 130B3093 2 x 130B2855 | 762 | 400 | P450 | 779 | 3020 | 2350 | < 80
130B3134 + 130B3135 130B2872 + 130B2873 | 130B3093 + 130B3094 130B2855 + 130B2856 | 861 | 450 | P500 | 857 | 3362 | 2717 | < 80
2 x 130B3135 2 x 130B2873 | 2 x 130B3094 2 x 130B2856 | 960 | 500 | P560 | 964 | 3704 | 3084 | < 80
3 x 130B3134 3 x 130B2872 | 3 x 130B3093 3 x 130B2855 | 1140 | 560 | P630 | 1090 | 4530 | 3525 | < 80
2 x 130B3134 + 130B3135 2 x 130B2872 + 130B2873 | 2 x 130B3093 + 130B3094 2 x 130B2855 + 130B2856 | 1240 | 630 | P710 | 1227 | 4872 | 3892 | < 80
3 x 130B3135 3 x 130B2873 | 3 x 130B3094 3 x 130B2856 | 1440 | 710 | P800 | 1422 | 5556 | 4626 | < 80
2 x 130B3134 + 2 x 130B3135 2 x 130B2872 + 2 x 130B2873 | 2 x 130B3093 + 2 x 130B3094 2 x 130B2855 + 2 x 130B2856 | 1722 | 800 | P1000 | 1675 | 6724 | 5434 | < 80

## 460V-60Hz
Code number AHF005 IP00/IP20 | Code number AHF010 IP00/IP20 | Filter current rating | Typical motor | VLT Power and Current Ratings |  | Losses |  | Acoustic noise | Frame size
|  | 50Hz |  |  |  | AHF005 | AHF010
|  | A | kW | kW | A | W | W | dBa | AHF005 | AHF010
130B1787 130B1752 | 130B1770 130B1482 | 10 | 3 | PK37-P4K0 | 1-7,4 | 131 | 93 | <70 | X1 | X1
130B1788 130B1753 | 130B1771 130B1483 | 14 | 7.5 | P5K5-P7K5 | 9,9+13 | 184 | 118 | <70 | X1 | X1
130B1789 130B1754 | 130B1772 130B1484 | 19 | 11 | P11K | 19 | 258 | 206 | <70 | X2 | X2
130B1790 130B1755 | 130B1773 130B1485 | 25 | 15 | P15K | 25 | 298 | 224 | <70 | X2 | X2
130B1791 130B1756 | 130B1774 130B1486 | 31 | 18.5 | P18K | 31 | 335 | 233 | < 72 | X3 | X3
130B1792 130B1757 | 130B1775 130B1487 | 36 | 22 | P22K | 36 | 396 | 242 | < 72 | X3 | X3
130B1793 130B1758 | 130B1776 130B1488 | 48 | 30 | P30K | 47 | 482 | 274 | < 72 | X3 | X3
130B1794 130B1759 | 130B1777 130B1491 | 60 | 37 | P37K | 59 | 574 | 352 | < 72 | X4 | X4
130B1795 130B1760 | 130B1778 130B1492 | 73 | 45 | P45K | 73 | 688 | 374 | < 72 | X4 | X4
130B1796 130B1761 | 130B1779 130B1493 | 95 | 55 | P55K | 95 | 747 | 428 | < 75 | X5 | X5
130B1797 130B1762 | 130B1780 130B1494 | 118 | 75 | P75K | 118 | 841 | 488 | < 75 | X5 | X5
130B1798 130B1763 | 130B1781 130B1495 | 154 | 90 | P90K | 154 | 962 | 692 | < 75 | X6 | X6
130B1799 130B1764 | 130B1782 130B1496 | 183 | 110 | P110 | 183 | 1080 | 743 | < 75 | X6 | X6
130B1900 130B1765 | 130B1783 130B1497 | 231 | 132 | P132 | 231 | 1194 | 864 | < 75 | X7 | X7
130B2200 130B1766 | 130B1784 130B1498 | 291 | 160 | P160 | 291 | 1288 | 905 | < 75 | X7 | X7
130B2257 130B1768 | 130B1785 130B1499 | 355 | 200 | P200 | 348 | 1406 | 952 | < 75 | X8 | X7
130B2259 130B1769 | 130B1786 130B1751 | 436 | 250 | P250 | 436 | 1852 | 1542 | < 77 | X8 | X7
130B1900 + 130B2200 130B1765 + 130B1766 | 130B1783 + 130B1784 130B1497 + 130B1498 | 522 | 315 | P315 | 531 | 2482 | 1769 | < 80
2 x 130B2200 2 x 130B1766 | 2 x 130B1784 2 x 130B1498 | 582 | 355 | P355 | 580 | 2576 | 1810 | < 80
130B2200 + 130B3166 130B1766 + 130B3167 | 130B1784 + 130B3166 130B1498 + 130B3165 | 671 | 400 | P400 | 667 | 2798 | 2080 | < 80
2 x 130B2257 2 x 130B1768 | 2 x 130B1785 2 x 130B1499 | 710 | 450 | P450 | 711 | 2812 | 1904 | < 80
2 x 130B3168 2 x 130B3167 | 2 x 130B3166 2 x 130B3165 | 760 | 500 | P500 | 759 | 3020 | 2350 | < 80
2 x 130B2259 2 x 130B1769 | 2 x 130B1786 2 x 130B1751 | 872 | 560 | P560 | 867 | 3704 | 3084 | < 80
3 x 130B2257 3 x 130B1768 | 3 x 130B1785 3 x 130B1499 | 1065 | 630 | P630 | 1022 | 4218 | 2856 | < 80
3 x 130B3168 3 x 130B3167 | 3 x 130B3166 3 x 130B3165 | 1140 | 710 | P710 | 1129 | 4530 | 3525 | < 80
3 x 130B2259 3 x 130B1769 | 3 x 130B1786 3 x 130B1751 | 1308 | 800 | P800 | 1344 | 5556 | 4626 | < 80
2 x 130B2257 + 2 x 130B2259 2 x 130B1768 + 2 x 130B1769 | 2 x 130B1785 + 2 x 130B1786 2 x 130B1499 + 2 x 130B1751 | 1582 | 1000 | P1M0 | 1490 | 6516 | 4988 | < 80

## 600V-60Hz
Code number AHF005 IP00/IP20 | Code number AHF010 IP00/IP20 | Filter current rating | Typical motor | VLT Power and Current Ratings |  | Losses |  | Acoustic noise | Frame size
|  | 50Hz |  |  |  | AHF005 | AHF010
|  | A | HP | kW | A | W | W | dBa | AHF005 | AHF010
130B5261 | 130B5229 | 15 | 10 | P11K | 15 | 298 | 224 | <70 | x3 | x3
130B5246 | 130B5212
130B5262 | 130B5230 | 20 | 16.4 | P15K | 19 | 335 | 233 | <70 | x3 | x3
130B5247 | 130B5213
130B5263 | 130B5231 | 24 | 20 | P18K | 24 | 396 | 242 | <70 | x3 | x3
130B5248 | 130B5214
130B5264 | 130B5232 | 29 | 24 | P22K | 29 | 482 | 274 | <70 | x4 | x4
130B5249 | 130B5215
130B5265 | 130B5233 | 36 | 33 | P30K | 36 | 574 | 352 | <70 | x4 | x4
130B5250 | 130B5216
130B5266 | 130B5234 | 50 | 40 | P37K | 49 | 688 | 374 | <70 | x5 | x5
130B5251 | 130B5217
130B5267 | 130B5235 | 58 | 50 | P45K | 58 | 747 | 428 | <70 | x5 | x5
130B5252 | 130B5218
130B5268 | 130B5236 | 77 | 60 | P55K | 74 | 841 | 488 | <72 | x6 | x6
130B5253 | 130B5219
130B5269 | 130B5237 | 87 | 75 | P75K | 85 | 962 | 692 | <72 | x6 | x6
130B5254 | 130B5220
130B5270 | 130B5238 | 109 | 100 | P90K | 106 | 1080 | 743 | <72 | x6 | x6
130B5255 | 130B5221
130B5271 | 130B5239 | 128 | 125 | P110 | 124 | 1194 | 864 | <72 | x6 | x6
130B5256 | 130B5222
130B5272 | 130B5240 | 155 | 150 | P132 | 151 | 1288 | 905 | <72 | x7 | x7
130B5257 | 130B5223
130B5273 | 130B5241 | 197 | 200 | P160 | 189 | 1406 | 952 | <72 | x7 | x7
130B5258 | 130B5224
130B5274 | 130B5242 | 240 | 250 | P200 | 234 | 1510 | 1175 | <75 | x8 | x8
130B5259 | 130B5225
130B5275 | 130B5243 | 296 | 300 | P250 | 286 | 1852 | 1288 | <75 | x8 | x8
130B5260 | 130B5226
2 x 130B5273 | 130B5244 | 366 | 350 | P315/P355 | 339/366 | 2812 | 1542 | <75 |  | x8
2 x 130B5258 | 130B5227
2 x 130B5273 | 130B5245 | 395 | 400 | P400 | 395 | 2812 | 1852 | <75 |  | x8
2 x 130B5258 | 130B5228
2 x 130B5274 | 2 x 130B5242 | 480 | 500 | P500 | 482 | 3020 | 2350
2 x 130B5259 | 2 x 130B5225
2 x 130B5275 | 2 x 130B5243 | 592 | 600 | P560 | 549 | 3704 | 2576
2 x 130B5260 | 2 x 130B5226
3 x 130B5274 | 2 x 130B5244 | 732 | 650 | P630 | 613 | 4530 | 3084
3 x 130B5259 | 2 x 130B5227
3 x 130B5274 | 2 x 130B5244 | 732 | 750 | P710 | 711 | 4530 | 3084
3 x 130B5259 | 2 x 130B5227
3 x 130B5275 | 3 x 130B5243 | 888 | 950 | P800 | 828 | 5556 | 3864
3 x 130B5260 | 3 x 139B5226
4 x 130B5274 | 3 x 130B5244 | 960 | 1050 | P900 | 920 | 6040 | 4626
4 x 130B5259 | 3 x 130B5227
4 x 130B5275 | 3 x 130B5244 | 1098 | 1150 | P1M0 | 1032 | 7408 | 4626
4 x 130B5260 | 3 x 130B5227
| 4 x 130B5244 | 1580 | 1350 | P1M2 | 1227 |  | 6168
4 x 130B5227

## 500-690V-50Hz
Code number AHF005 IP00/IP20 | Code number AHF010 IP00/IP20 | Filter current rating | VLT Power and Current Ratings | [5 empty] | Losses |  | Acoustic noise | Frame size
|  | 50Hz | Typical motor size | 500-550V |  | Typical motor size | 551-690V |  | AHF005 | AHF010
|  | A | kW | kW | A | kW | kW | A | W | W | dBa | AHF005 | AHF010
130B5000 | 130B5297 | 15 | 7.5 | P11K | 15 | 15 | P15K | 16 | 298 | 224 | <70 | x3 | x3
130B5088 | 130B5280
130B5017 | 130B5298 | 20 | 11 | P15K | 19.5 | 18.5 | P18K | 20 | 335 | 233 | <70 | x3 | x3
130B5089 | 130B5281
130B5018 | 130B5299 | 24 | 15 | P18K | 24 | 22 | P22K | 25 | 396 | 242 | <70 | x3 | x3
130B5090 | 130B5282
130B5019 | 130B5302 | 29 | 18.5 | P22K | 29 | 30 | P30K | 31 | 482 | 274 | <70 | x4 | x4
130B5092 | 130B5283
130B5021 | 130B5404 | 36 | 22 | P30K | 36 | 37 | P37K | 38 | 574 | 352 | <70 | x4 | x4
130B5125 | 130B5284
130B5022 | 130B5310 | 50 | 30 | P37K | 49 | 45 | P45K | 48 | 688 | 374 | <70 | x5 | x5
130B5144 | 130B5285
130B5023 | 130B5324 | 58 | 37 | P45K | 59 | 55 | P55K | 57 | 747 | 428 | <70 | x5 | x5
130B5168 | 130B5286
130B5024 | 130B5325 | 77 | 45 | P55K | 71 | 75 | P75K | 76 | 841 | 488 | <72 | x6 | x6
130B5169 | 130B5287
130B5025 | 130B5326 | 87 | 55 | P75K | 89 |  |  |  | 962 | 692 | <72 | x6 | x6
130B5170 | 130B5288
130B5026 | 130B5327 | 109 | 75 | P90K | 110 | 90 | P90K | 104 | 1080 | 743 | <72 | x6 | x6
130B5172 | 130B5289
130B5028 | 130B5328 | 128 | 90 | P110 | 130 | 110 | P110 | 126 | 1194 | 864 | <72 | x6 | x6
130B5195 | 130B5290
130B5029 | 130B5329 | 155 | 110 | P132 | 158 | 132 | P132 | 150 | 1288 | 905 | <72 | x7 | x7
130B5196 | 130B5291
130B5042 | 130B5330 | 197 | 132 | P160 | 198 | 160 | P160 | 186 | 1406 | 952 | <72 | x7 | x7
130B5197 | 130B5292
130B5066 | 130B5331 | 240 | 160 | P200 | 245 | 200 | P200 | 234 | 1510 | 1175 | <75 | x8 | x8
130B5198 | 130B5293
130B5076 | 130B5332 | 296 | 200 | P250 | 299 | 250 | P250 | 280 | 1852 | 1288 | <75 | x8 | x8
130B5199 | 130B5294
2 x 130B5042 | 130B5333 | 366 | 250 | P315 | 355 | 315/355 | P315/P355 | 333/368 | 2812 | 1542 | <75 |  | x8
2 x 130B5197 | 130B5295
2 x 130B5042 | 130B5334 | 395 | 315 | P355 | 381 | 400 |  |  | 2812 | 1852 | <75 |  | x8
2 x 130B5197 | 130B5296
130B5042 + 130B5066 | 130B5330 + 130B5331 | 437 | 355 | P400 | 413 | 500 | P400 | 395 | 2916 | 2127
130B5197 + 130B5198 | 130B5292 + 130B5293
130B5066 + 130B5076 | 130B5331 + 130B5332 | 536 | 400 | P450 | 504 | 560 | P500 | 482 | 3362 | 2463
130B5198 + 130B5199 | 130B5292 + 130B5294
2 x 130B5076 | 2 x 130B5332 | 592 | 450 | P500 | 574 | 630 | P560 | 549 | 3704 | 2576
2 x 130B5199 | 2 x 130B5294
130B5076 + 2x130B5042 | 130B5332 + 130B5333 | 662 | 500 | P560 | 642 | 710 | P630 | 613 | 4664 | 2830
130B5199 + 2x130B5197 | 130B5294 + 130B5295
4 x 130B5042 | 2 x 130B5333 | 732 | 560 | P630 | 743 | 800 | P710 | 711 | 5624 | 3084
4 x 130B5197 | 2 x 130B5295
3 x 130B5076 | 3 x 130B5332 | 888 | 670 | P710 | 866 | 900 | P800 | 828 | 5556 | 3864
3 x 130B5199 | 3 x 130B5294
2 x 130B5076 + 2 x 130B5042 | 2 x 130B5332 + 130B5333 | 958 | 750 | P800 | 962 | 1000 | P900 | 920 | 6516 | 4118
2 x 130B5199 + 2 x 130B5197 | 2 x 130B5294 + 130B5295
6 x 130B5042 | 3 x 130B5333 | 1098 | 850 | P1M0 | 1079 |  | P1M0 | 1032 | 8436 | 4626
6 x 130B5197 | 3 x 130B5295

## Mechanical dimensions
IP20: Ventilation fan mounted:
The new AHF enclosure type and sizes |  |  |  | 380 V, 60 Hz 400 V, 50Hz | 460 V, Hz | Fan
Enclosure | Dimensions in mm |  |  | Current | Current
Type | A (height) | B (width) | C (depth) | [A] | [A] | AHF010 | AHF005
X1 | 332 | 190 | 206 | 10 | 10 | no | no
X2 | 436 | 232 | 248 | 14 | 14 | no | no
X3 | 594 | 378 | 242 | 22 | 19 | inside | outside
X4 | 634 | 378 | 333 | 29 | 25 | inside | outside
X5 | 747 | 418 | 333 | 34 | 31 | inside | inside
X6 | 778 | 418 | 396 | 40 | 36 | inside | inside
X7 | 909 | 468 | 449 | 55 | 48 | inside | inside
X8 | 911 | 468 | 549 | 66 | 60 | inside | inside
|  |  |  | 82 | 73 | inside | inside
The existing AHF enclosure type and sizes |  |  |  | 96 | 95 | inside | inside
Enclosure | Dimensions in mm |  |  | 133 | 118 | inside | inside
Type | A (height) | B (width) | C (depth) | 171 | 154 | inside | inside
B | 453 | 165 | 242 | 204 | 183 | inside | outside
C | 698 | 296 | 220 | 251 | 231 | inside | outside
D | 938 | 354 | 220 | 304 | 291 | inside | outside
E | 1046 | 397 | 400 | 325 | 355 | inside | outside
F | 1152 | 458 | 419 | 380 | 380 | inside | outside
G | 1322 | 458 | 419 | 480 | 436 | inside | outside
H | 1352 | 522 | 409
IP20: Ventilation fan mounted:
|  |  |  | 600V, 60Hz 500-690V, 50Hz | Fan
Current
|  |  |  | [A] | AHF010 | AHF005
|  |  |  | 15 | inside | inside
|  |  |  | 20 | inside | inside
|  |  |  | 24 | inside | inside
|  |  |  | 29 | inside | inside
|  |  |  | 36 | inside | outside
|  |  |  | 50 | inside | inside
|  |  |  | 58 | inside | outside
|  |  |  | 77 | inside | inside
|  |  |  | 87 | inside | inside
|  |  |  | 109 | inside | inside
|  |  |  | 128 | inside | outside
|  |  |  | 155 | inside | outside
|  |  |  | 197 | inside | outside
|  |  |  | 240 | inside | outside
|  |  |  | 296 | inside | outside
|  |  |  | 366 | outside | -
|  |  |  | 395 | outside | -